## Slide 1: Open Compute +48V Busbar Discussion
Engineered
Power Solutions

## Slide 2
  Opportunities with Open Rack
    There are a few areas within the Open Rack 2.0 standard that remain undefined. In terms of the mechanical requirement of the busbar assembly, there is a gap where rack mount details are missing. This means that ever rack mounts to every busbar differently.
    It is difficult to design a busbar that will work in many applications for OCP. This is compounded when working towards an “OCP Accepted” certification. The reason is that to be “Accepted” the certification is granted per part number and not general application
    This is very difficult to achieve at a busbar level due to many variables that tend to be customer specific:
      Power Requirements
      Height (OU, OUI, etc.)
      Location of Power Supplies
      Mechanism/Locations for attaching the Power Supplies
      Mounting Criteria for Busbar
Each Power Section (3) can have 1, 2 or 3 busbars

## Slide 3
  OCP Specification
    To expand upon Rittal’s Options: Amphernol is developing higher power busbars
      50 kW
      60 kW
      100 kW
    Each of these will add additional SKU Levels:

## Slide 4
Busbars
PowerLug or
Busbars from
The Power Supply
Protective Cage
Blind Mate Guides
36 kW Busbar would require (3) 4/0 wires
for each potential
Future question is with higher kW requirements, will 3 posts be sufficient?
Will the spacing need to change to accommodate larger wire gage?
May need to change
these dimensions
and/or add studs?
Management of Power Supply Connections

## Slide 5
Example of OCP 48V Busbar SKU Matrix
P/N: BBOCP 48 AA BBB PSCCDD EE
BusBar OCP
48 = 48V
Watts
15 = 15kW
36 = 36kW
50 = 50kW
Rack OU or OUI
XXU= “#”OU
XXI = “#”OUI
Power Supply
Location
CC = OU(I) of first PS
DD = OU(I) of 2nd PS
Rack Manufacturer
CW = Chatsworth
DT = Delta
EN = Emerson
FX = Flex
RC = Rack Space
RS = Rack Solutions
RT = Rittal
TL = Telect

## Slide 6
    Not all Power Ratings are the Same!
    Regarding the Topic of Power rating for an entire rack. A 36kW rack for example can be configured with a Single Power Zone, a Split Single (Dual), or (3) 12kW Power Zones.
    It is our suggestion that the number of Power Zone(s) should be considered when rating the busbar in context to the rack. A single 36kW power zone bubar will have more copper mass than a Split Single Zone 18kW busbar.
Power Zones
Single Power Zone
PS
PS
Busbar
PS
Dual Power Zone
Busbar
PS

## Slide 7
    Another challenge is the location of the Power Supply(ies). This becomes a particular challenge with the full length busbars (~42 OU).
    As a power solutions provider, the preference would be a central location to minimize the copper usage or increase the power availability
      For example, the design of a 36 kW busbar with the power supplies centrally located will minimize the copper needed to support this power level (half the power for each busbar leg) vs. locating the Power Supplies either top or bottom which will require the support the full power (~950A at minimum voltage)
Power Supply Location
PS Centrally Located
PS Top Located
PS
PS
Busbar
Larger Busbar

## Slide 8
  Busbar current ratings can vary from vendor to vendor. Should we reference in section 3.2 for the 48V OCP spec a variable for determining power rating based on cross section area of copper. A 30 degree C T Rise.
  In the development of Busbars we use a very easy to remember formula of:
  5A / mm2
  This has been supported by Simulation and Load testing by groups within Amphenol (AIPC and AFCI).
Copper Sizing Calculation

## Slide 9
Touch Proof Requirement – Open Rack 2.0 Section 2.5
  IEC60950 requires a finger probe test as shown in the below images.

## Slide 10
THANK YOU!
Connectors
Power
Assemblies
PowerLugs
Busbars
Cable Assemblies